Engineering Specification

Model JCR Standard and Quick Response Automatic Sprinklers

Pendent and Upright Positions

Sprinklers shall be a standard coverage, standard and quick response [upright] [pendent] that is ABNT and UL-BR certified, based on ABNT NBR16400:2022, with the quality management in the production process certified by ABNT / ISO9001:2015 and FM according to FM Approvals Standard: Class Series 2000, for occupation of areas with risks [light] [ordinary] [extraordinary]. Sprinkler frame and deflector shall be of brass frame construction having a [½”/15mm] [¾”/20mm] NPT/BSP thread. The water sealing member applied between the slide body and the shutter element which supports the thermal bulb glass in order to prevent pressure leaks, is a type washer-coated teflon, is called Belleville. The thermosensitive element should be the type of bulb glass, resistant vertically to the operating pressure of the hydraulic pipes (12 to 15bar), with temperature rating shall be [155 (F (68 (C)] [175 (F (79 (C)] [286 (F (141 (C)]. Sprinklers shall have a nominal K-factor (flow and pressure relation) of [5.6 (US) / 81.0 (metric)] [8.0 (US) / 115 (metric)]. Standard finish: [Chrome-plated] [Natural]. Refer to “JCR - Technical Bulletin” for identification technical information with respect to type of response, position, diameter, temperature and finishing. The diameters of [½"/15mm] [¾"/20mm] correspond to the K factors [5,6US (80 metric)] and [8.0US (115 metric)] respectively.

HOW TO SPECIFY A REFERENCE MODEL SPRINKLER JCR:

| Model | Response type | Position | Diameter (mm) | Temperature (ºC) | Finishing | Listing & Approvals |
| --- | --- | --- | --- | --- | --- | --- |
| JCR | (QR) Quick Response (Empty) Standard Response | (H) Pendent (F) Upright | 15 20 | 68 79 141 | NA CR | ABNT UL-BR FM |

Example: A sprinkler JCR model, type fast response, its installed position is pending, 1/2" thread, drive temperature of 68 °C and natural finish is represented as follows:

| Model | Response type | Position | Diameter (mm) | Temperature (ºC) | Finishing | Listing & Approvals |
| --- | --- | --- | --- | --- | --- | --- |
| JCR | QR | H | 15 | 68 | NA | ABNT, UL-BR, FM |

Specifying, for example, the same product by changing the type of response to standard response would thus:

| Model | Response Type | Position | Diameter (mm) | Temperature (ºC) | Finishing | Listing & Approvals |
| --- | --- | --- | --- | --- | --- | --- |
| JCR | EMPTY | H | 15 | 68 | NA | ABNT, UL-BR, FM |